## Construction Documents Minimum Design Guidelines

TABLE R301.2 (1) amended

## Climatic And Geographic Design Criteria

| ROOF SNOW LOAD | WIND | SEISMIC DESIGN CATEGORYf,g | SUBJECT TO DAMAGE FROM | WINTER DESIGN TEMPf | FLOOD HAZARDSh |
| --- | --- | --- | --- | --- | --- |
|  | Speede (mph). |  | Weatheringa | Frost line depthb | Termitec | Decayd |  |  |
| 0 | 90 Exposure C | B | Negligible | Final Grade | Moderate to heavy | None to slight | 34 degrees |  |

## Building Code Design Data

All construction within Scottsdale shall comply with the following codes and amendments per their adopting ordinances:

| 2012 International Building Code | (ord. # 4059 ) |
| --- | --- |
| 2012 International Residential Code | (ord. # 4060 ) |
| 2012 International Fire Code | (ord. # 4045 ) |

## APPLICANT:  Correct plans where the following items have been checked.

- Provide Civil Site plan.

- Refer to plan set for red lines.  Correct plans as marked or submit equivalent alternate corrections.

- IRC sections indicated are for your convenience in detailing code requirements.

- Do not quote code IRC Sections in lieu of providing plan set notes and revised details.

- IMPORTANT:  Please return all documents indicated on the Resubmittal Checklist.

- Plan set is incomplete.  Next submittal may require additional review(s).

- Plans must be readable and to “scale”.

- Specification books on Single Family Plan checks are not acceptable.

- Place all required notes on the drawings.

- Provide a True North Arrow and an Orientation North Arrow on site plans and floor plans.

A.	Standard Plans

  - Provide a soils report and a compaction tests for the subdivision.

  - Per the soils report provide over-excavation and / or re-compaction for foundations and slabs on grade.

  - Place the following notes in bold type on the foundation plan and floor plan sheets:

- This standard plan is not approved for locations within 5 feet of an adjacent property line.  (NOTE:  Zoning setbacks or Design Review Board stipulations may be more restrictive.) (R302.1)

- Projections shall not extend more than 12” into the areas where openings are prohibited.

- Overhangs and projections within 5’ of the property line shall be of one-hour (fire rated) on the underside.

- Eaves over required bedroom egress windows shall not be within 30” of the side and rear property lines.

  - Provide a continuous three foot wide path of travel from all bedroom egress windows to a public way.

  - Show minimum allowable dimensions from stem wall to property lines on foundation plan.

  - Remove all parcel/lot specific information from plan set. (i.e. site plan).

  - The cover sheet must have key plans drawn to scale indicating each possible combination of footprint options with corresponding building ridge lines to ensure conformance with varying lot configurations.

B. Add/ Alt/ Remodels

- Provide scope of work. (IBC 107.2.1 amend.)

- Provide separate existing and demolition plans. (IBC 107.2.1 amend.)

- Clearly identify throughout, existing vs. new vs. remodeled area.  (IBC 107.2.1 amend.)

- Complete and return fire sprinkler worksheet. (IFC 903)

- Address smoke and CO detectors throughout house with additions/alterations/remodels. (R314-315).

C.	Site Plan

- Provide a complete site plan, grading and drainage where required. (IBC 107.2.5, R302.1).

- Provide a complete project address. (R319.1)

- Show location of structure(s) with setback dimensions on site plan. (IBC 107.2.5, R302.1).

- Show location of all site fences and retaining walls on site plan.  Provide lineal footage of fences and retaining walls. (IBC 107.2.5)

- Reference on site plan, structural details for each site retaining wall and fence. (IBC 107.2.5).

- Provide structural calculations for retaining walls. City of Scottsdale, Administrative Policy 13-3.

- Show sewer tap location at street.  (P3008.1)

- Show and identify next upstream manhole rim location and elevation, address backwater valve. (P3008.1).

- If septic system, provide copy of septic system permit application from Maricopa County.  (P2602.1)

- When enclosing pool, provide minimum 3-foot wide, minimum 60-inch high, out-swinging, self-closing gate. (AG103.1).

D. GREEN BUILDING (IBC 102.4.3)

- Provide a separate plan sheet listing the minimum 28 "green" building requirements and the options selected from the 300 available.  Include the points permitted for each selection and a total summary (minimum 50 points for entry level and 100 points for advanced level)

- Incorporate the "green" building requirements with-in the plan design, including notes and details, (i.e. carbon monoxide detectors locations and 1.3 or less gal/flush or dual-flush toilets, etc).

- Provide the most current Testing or Evaluation Report for the Building Product(s), i.e. Rastra, Eco-block, Tech-Block, Etc.

- Incorporate Designs, Details, Instructions and Requirements from the Evaluation Report(s) onto the plans and reference where applicable.

- Provide REScheck or equal for each house.

- Place the following note in large text on the Plan Sheets (Floor, Foundation, Roof Framing):

NOTE: To maintain "Green Building" status, separate "Green Building" inspections are required prior to covering work.

E.	Floor plans

##### Doors and Windows

- Provide a 1-3/8” solid door …self-closing, self-latching, between residence and garage. (R302.5.1 amend.).

- Provide permanent landing at exterior doors. (R311.3.2 amend).

- Doors shall not open directly between a sleeping room and a garage. (R302.5.1).

- Shower doors shall have safety glazing; hinged shower doors shall open outward. (R308.4.5, P2708.1).

- Provide and identify all required safety glazing. (R308).

- Indicate emergency escape and rescue openings in basements and bedrooms. (R310.1).

- Show direction of door swing. (R311.3.2 amended).

- Show size of each window and type of operation. (R303.1, 310.1.1-.4).

- Show type of structural silicone for butt-glazed windows. (Interpretation 98-11).

- Glazing maximum U-factor 0.40, Solar Heat Gain Coefficient (SHGC) Maximum 0.25 (TN1102.1.1)

- Opaque doors separating conditioned and unconditioned space- maximum U-factor 0.40.  (TN1102.1.1).

- Skylight - maximum U-factor 0.65.  Provide manufacture and ICC-ES number.  (TN1102.1.1).

##### Light and Ventilation

- Provide required natural light and ventilation for habitable rooms (R303.1).  Light: 8%, ventilation: 4%.

- Provide mechanical exhaust ventilation for bathrooms, water closet rooms, laundry room, and kitchen, ducted direct to outside. (R303.3 amended, (M1507.2).

- Provide attic ventilation per (R806.1) unless insulation is applied on the under-side of roof sheathing. (R806.5 #5).

##### Stairways, handrails, guardrails

- Show handrail, notes and dimensions where required (R311.7.8).

- Show guardrails where required. (R312.1, .2).

- Provide a floor or landing at the top and bottom of each stairway. (R311.7.6).

- Provide code complying stairways; address tread and riser dimensions per type of stairway. (R311.7).

- Provide stairway illumination per (R303.7.9)

- Stairway maximum 12’ vertical rise between floor/landing (R311.7.3).

##### Fire Places/Gas Appliances

- Provide manufacture, model number and ICC report or equal for each fireplace. (R1002, 1004, 1005).

- Provide a permanently installed approved decorative appliance/gas log set. (R1004.4).

- Fireplace dampers: Where a listed decorative appliance is installed, the fireplace damper opening shall comply with listed decorative appliance manufacture’s installation instructions.  (G2453.1)

- Decorative shrouds shall not be installed at the termination of chimneys of factory-built fireplaces except where listed and labeled for such use. (R1004.3)

- Provide outside combustion air for interior fireplaces. (R1006.2).

##### General Floor Plan

- Show ceiling heights for all rooms, spaces and hallways. (R305).

- Show minimum clearances from centerline of water closets to finished wall, cabinets, and other plumbing fixtures. (R307.1, P2705.1).

- Gypsum Board applied to a ceiling shall be 1/2” when framing members are 16” o.c. or 5/8” when framing members are 24” o.c. or use labeled 1/2” sag-resistant gypsum ceiling board. (Table R702.3.5 (d)).

##### Manufacturers’ Installation Instructions

- Manufacture’s installation instructions, as required by this code, shall be available on the job site at the time of inspection (R106.1.2)

- RANGES AND COOKTOPS: Show note on plans.

-Provide a listed and approved range and/or cooktop unit installed in accordance with the listing and with the manufacturer’s installation instructions.  VERIFY AND MAINTAIN REQUIRED HORIZONTAL AND VERTICAL CLEARANCES ABOVE THE FINISHED COUNTERTOP SURFACE BEFORE ORDERING OR INSTALLING CABINETS-.

F.	Braced/Shear wall Plan

- Provide a complete braced/shear wall plan and reference a braced /shear wall schedule at each braced/shear wall location. (R602.10).

- Braced/Shear wall schedule to include anchor bolts, holdowns, studs and spacing, sheathing and nailing.  (T.602.3(1)), (R403.1.6, 403.1.6.1).

- Address ‘alternate braced wall panels’ per (R602.10.6).

- Coordinate post locations with holdowns on foundation plan. (R602.11.1).

- Show and identify each required holdown on foundation plan.

- Provide Wood-Stud wall Engineering Analysis for bearing walls Over 10 Feet High (T. R602.3 (5)).

G.	Elevation Plan

- Provide minimum of four elevation drawings of building, typical front, back, left, right.

- Show building heights and dimensions.

- Show and label all exterior surface building materials. (R703).

- Show manufacture, model number and ICBO/ICC/NER Report Number for stucco, roof materials, stone veneer. (R703.7).

- Provide weather flashing/proofing and exterior wall penetrations/openings. (R703.1, 703.2, 703.8).

H. Sections

- Provide minimum two building cross sections.

- Cut cross-sections on foundation, floor and roof framing plans.

- Foam plastics shall be separated from attics and crawl spaces. (R316.4).

- Show required fire blocking on each section. (R602.8).

- Show height dimensions on each cross-section.

- Label all rooms, spaces, and hallways on each section.

- Provide and reference/key structural details for critical connections for cross-sections.

I.	Wall Construction

- Provide a cross section detail and wall legend for each type of wall.

- Callout exterior materials, including, stucco system, lath, building paper, foam, and sheathing where required. (R703).

- Specify on plans, interior wall materials. (R702).

- Specify on plans, interior wall construction, coverings, and backings for tile and in wet locations. (R702.1).

- Provide weepscreed and dimensions from soil and paved surfaces. (R703.6.2.1).

- Provide nailing schedule. (R602.3 (1)).

J.	Foundation Plan

- For single-family custom submittal, provide a soils report or a soils waiver signed by owner.

- Provide a complete fully dimensioned and detailed foundation plan.

- Address foundation drainage per (R405.1).

- Address foundation damp proofing (R406.1)

- Show isolated footing dimensions, and reinforcing. (Table R403.1 amended).

- Show note: Exterior and interior footings shall bear minimum 18 inches below undisturbed soil or engineers certified compacted fill. (Table R 403.1).

- Show required reinforcing steel for all footings and stem. (R 403.1.3.1).

- Reference a complete set of structural details, footing, stem, turndown, pad footing, post at stem…

- Clearly show, dimension and detail interior bearing footings and shearwall footings.

- Clearly show each required post location on foundation plan, coordinate with shearwall and roof framing plans.

- Clearly show and label each required holdown on foundation plan. (R403.1.6).

- Show and detail building retaining walls and basement and foundation walls, including drainage. (R 405.1)

- Provide any/all slab elevations.

K.	Floor and Roof Framing Plans

- Provide a complete fully detailed floor and/or roof-framing plan. (R106 amended).

- Clearly identify all framing members, including posts/columns, headers, beams, joists, and trusses. (R106 amended).

- Clearly show each required post and size, coordinate with foundation plan.

- Show and identify posts from above framing.

- Show floor-to-floor tie, mechanical connectors.

- Clearly show and identify all truss/joist hangers.

- Cleary show and identify beam to post mechanical connectors.

- Clearly show and key detail reference(s) for each beam to post, beam-to-beam, and girder to beam connections.

- Detail typical truss/joist to wall, beam, and girder connections.

- If pre-qualifying conditions are met, deferred submittals for truss design drawing may be allowed per (R802.10.1.1 amended).

- Show lateral full height blocking at braced/shear wall line for joists, rafters and trusses.

- Framing details shall reflect types of framing members, trusses flat and sloped, I-joists, dimension lumber rafters…

- Show stair mechanical attachment at top and bottom.

- Framing members to accommodate masonry fireplace clearances to combustibles.  (Table R1001.1).

- Provide seismic strap per (R1003.4.1).

- Provide detail showing how lateral forces are transferred from roof diaphragm into shear wall.

- Identify all trusses used as drag struts, and show loads on framing plan.

- Framing members to accommodate mechanical equipment requirements if installed in attic.

L.	Structural Calculations

- Provide the following structural engineering calculations:

- Gravity loads analysis.

- Lateral loads analysis.

- Retaining wall calculations per policy #13-3.

- Provide special inspections per (IBC Ch. 17).

M. Mechanical plans

- Show mechanical equipment and water heaters on 18-inch platform if placed in garage or room with direct access to garage. (M1307.3).

- Provide combustion air and show hi and low vent opening sizes for gas fuel appliances located in confined spaces. (G2407).

- Provide and reference approved detail for gas piping to gas island cooktop. (G2415.14).

- Provide kitchen exhaust fan vented direct to outside. (M1507.2 amend. T.M1507.4).

- Provide minimum 78% AFUE (Annual Fuel Utilization Efficiency) for weatherized gas heating equipment, Non-weatherized equipment minimum 80% AFUE. (T.N1105.5.2 (1)g).

- Provide minimum 13 SEER (Seasonal Energy Efficiency Ratio) for air conditioning equipment. ((T.N1105.5.2 (1) h).

- Provide HVAC equipment sizing calculations.

Heating and cooling equipment shall be sized in accordance with ACCA Manual S based on building loads calculated in accordance with ACCA Manual J or other approved calculation methodologies. (N1103.6)

- Duct systems serving heating, cooling and ventilation equipment shall be installed in accordance with the provisions of this section and ACCA Manual D or other approved methods. (M1601.1)

- Show supply and return air ducts and registers. (IBC 107.2.1 amend.)

- Supply and return ducts shall be insulated to a minimum R-8.  Ducts in floor trusses shall be insulated to minimum R-6. (N1103.2.1).

N.	Electrical Plan

- Provide a complete Electrical Plan (IBC 107.2 amended).

- Provide fully noted plan showing, all required receptacles, light fixtures, switches, exhaust fans, smoke detectors, service panels and sub-panels. (E3703, E3901).

- Provide notes and symbols legend.

- Show and label all required GFCI and WP/GFCI receptacles. (E3901.2, E3902, E3903).

- Show and label all required AFCI circuits. (E3902.12).

- In areas specified in Section E3901.1, 125-volt, 15- and 20-ampere receptacles shall be listed tamper-resistant receptacles. (E4002.14)

- Provide minimum 75% high efficacy lamps. (N1104.1).

- Show and label all WP/DP lighting fixtures as SUITABLE FOR WET OR DAMP LOCATIONS accordingly. (E4001.7).

- Show and label all smoke alarms. Smoke alarms shall be installed in the following locations: 1. In each sleeping room. 2. Outside each separate sleeping area in the immediate vicinity of the bedrooms. 3. On each additional story of the dwelling, including basements and habitable attics but not including crawl spaces and uninhabitable attics. In dwellings or dwelling units with split levels and without an intervening door between the adjacent levels, a smoke alarm installed on the upper level shall suffice for the adjacent lower level provided that the lower level is less than one full story below the upper level. (R314).

- Show and label all carbon monoxide alarms, an approved carbon monoxide alarm shall be installed outside of each separate sleeping area in the immediate vicinity of the bedrooms in dwelling units within which fuel-fired appliances are installed and in dwelling units that have attached garages. (R315).

- Provide a UFER ground encased in concrete footing. (E3608.1.2).

- For Electrical Services greater than 400 amps, PROVIDE ELECTRICAL LOAD CALCULATIONS.

- Provide an ELECTRICAL SINGLE LINE DIAGRAM for Services 200 amps and larger.

O.	Plumbing Plan

- Provide a single line gas-piping diagram; include all gas burning appliances and BTUs of each appliance, show pipe lengths and sizes from gas meter to each branch line and to each appliance. (G2413).

- Show type of gas piping. (G2414).

- Do not place gas piping under slab. (G2415.14).

- Provide approved detail for gas piping to kitchen island gas cook top. (G2415.14).

- Provide minimum R-3 insulation to hot water pipes. (N1103.4).

- Show all drainage/sewer piping materials. (Tables P3002.1, P3002.2)

- Provide low flow plumbing fixtures. (P2903.2).

- Provide roof drains and over-flow/scuppers. (R903.4).

- Storage-tank type water heaters shall be installed with a drain pan and drain line. (P2801.5).

- WH-pan drain-line shall terminate per (P2801.5.2).

      - Fire Sprinklers

- Provide fire sprinklers per (IFC 903.).

      - Energy Requirements

- Complete and return REScheck or equal report.   Compliance shall be demonstrated by a passing score. (T.N1102.1.4).

- Comply with insulation requirements. (T.N1102.1.1.)

- Comply with fenestration requirements. (T.N1102.1.1.)

- At least one thermostat shall be provided for each separate heating and cooling system.  (N1103.1).

- A minimum of 75 percent of the lamps in permanently installed lighting fixtures shall be high-efficacy lamps or a minimum of 75 percent of the permanently installed lighting fixtures shall contain only high-efficacy lamps. (N1104.1).

- Recessed luminaires installed in the building thermal envelope shall be sealed to limit air leakage between conditioned and unconditioned spaces. All recessed luminaires shall be IC-rated and labeled as having an air leakage rate not more than 2.0 cfm... All recessed luminaires shall be sealed with a gasket or caulk between the housing and the interior wall or ceiling covering.  (N1102.4.4).

- The building shall be provided with ventilation that meets the requirements of Section M1507 or with other approved means of ventilation. Outdoor air intakes and exhausts shall have automatic or gravity dampers that close when the ventilation system is not operating. (N1103.5).

- The building or dwelling unit shall be tested and verified as having an air leakage rate of not exceeding 5 air changes per hour.  Testing shall be conducted with a blower door at a pressure of 0.2 inches w.g. (50 Pascal’s).  Testing shall be conducted by an approved third party, (BPI or RESNET certified).  A written report of the results of the test shall be signed by the party conducting the test and provided to the building official. Testing shall be performed at any time after creation of all penetrations of the building thermal envelope. (N1102.4.2).

- Ducts, air handlers, and filter boxes shall be sealed. Joints and seams shall comply with Section M1601.4.1.  Provide Duct tightness testing conducted by an approved third party testing agency (BPI or RESNET certified) and the signed written results shall be submitted to the Code Official prior to the Building Final. (N1103.2.2).  Duct tightness shall be verified by either of the following:

1.	Post-construction test: Total leakage shall be less than or equal to 4 cfm per 100 square feet of conditioned floor area when tested at a pressure differential of 0.1 inches w.g. (25 Pa) across the entire system, including the manufacturer’s air handler enclosure. All register boots shall be taped or otherwise sealed during the test.

2.	Rough-in test: Total leakage shall be less than or equal to 4 cfm per 100 ft2 of conditioned floor area when tested at a pressure differential of 0.1 inches w.g. (25 Pa) across the system, including the manufacturer’s air handler enclosure. All registers shall be taped or otherwise sealed during the test. If the air handler is not installed at the time of the test, total leakage shall be less than or equal to 3 cfm per 100 square feet of conditioned floor area.

- Supply and return ducts shall be insulated to a minimum R-8.  Ducts in floor trusses shall be insulated to minimum R-6. (N1103.2.1).

- Provide Minimum R-3 insulation on hot water pipes. (N1103.4).

- Circulating hot water systems shall be provided when the length of hot water piping or tubing from the source of hot water to the furthest fixture exceeds 21 feet for a ¾ inch line, 32 feet for a 5/8 inch line, 43 feet for a ½ inch line and 50 feet for a 3/8 or less inch line. When the hot water distribution system contains more than one pipe or tube size, the largest size shall be used for determining the maximum allowable length before a circulating hot water system is required. The circulating system shall be equipped with an automatic or readily accessible manual on switch and a temperature sensor activated shut-off that can automatically turn off the hot-water circulating pump when the set temperature is reached. For the purpose of this section, the source of hot water shall be considered to be a water heater, boiler, circulation loop piping, distribution manifold or heat-traced piping.  (N1103.4.1 amended.).

REQUIRED RESIDENTIAL NOTES

The following notes shall be incorporated into the plans. If these notes are reproduced on the plans as a block, it will facilitate the review of the project. The notes are available and can be downloaded from. http://www.scottsdaleaz.gov/bldgresources/planreview

# PLACE THE FOLLOWING REQUIRED NOTES ON THE DRAWING

| 2012 International Building Code | (ord. # 4059 ) |
| --- | --- |
| 2012 International Residential Code | (ord. # 4060 ) |
| 2012 International Fire Code | (ord. # 4045 ) |

- All products listed by ICC/N.E.R. number(s) shall be installed per the report and manufacturer’s written instructions.  Product substitution(s) for product(s) listed shall also have an ICC approved evaluation report(s) or be approved.

- Provide fire protection sprinkler system. (IFC 903. Amend.).

- Miscellaneous site structures, pools, spas, fences, site walls, retaining walls, and gas storage tanks may require separate permits.

- All exits to be operable from the inside without the use of a key or special knowledge. (310.1.4)

- Doors leading into house from garage shall be 20 minute rated or equal, self-closing, self-latching. (R302.5.1 Amend.).

- Exterior wall penetrations by pipes, ducts or conduits shall be caulked. (R307.6)

- Lumber shall bear an approved grading stamp (R502.1).

- Bottom wood sill plates shall be pressure treated or equal.  Exterior wall bottom sill plates shall bear/extend minimum 6 inches above finish grade. (R317.1, No. 3).

- When structural plans are not sealed by registered design professional, provide engineered truss designs for all prefabricated trusses for review and approval by the City of Scottsdale. (R802.10.1).

- Fire blocking shall comply with (R602.8).

- Masonry Bed and head joints…shall be 3/8 inch-thick, the thickness of the bed joint of the starting course placed over foundations shall not be less than 1/4 inch and not more than ¾ inch.  Mortar joint thickness shall be within the following tolerances from the specified dimensions: 1. Bed joint: + 1/8 inch. 2. Head joint: 1/4 inch + 3/8 inch. 3. Collar joints: 1/4 inch + 3/8 inch. (R607.2.1).

- Windows located more than 72” above finished grade shall have the lowest part of clear opening of the window to be minimum 24 inches above the floor in which it serves. (R312.2.1).

- Gypsum board applied to a ceiling shall be 1/2” when framing members are 16” o.c. or 5/8” when framing members are 24” o.c. or use labeled 1/2” sag-resistant gypsum ceiling board. Table R702.3.5 (d).

- Showers and tub-shower combinations shall be provided with individual control valves of the pressure balance or thermostatic mixing valve type.  (P2708.3).

- Shower area walls shall be finished with a smooth, hard non-absorbent surface, such as ceramic tile, to a height of not less than 72 inches above the drain inlet.  Water-resistant gypsum board shall not be installed over a vapor retarder in a shower or tub compartment.  Cement, fiber-cement or glass mat gypsum backers installed in accordance with mfgrs’ recommendations shall be used as backers for wall tile in tub and shower areas and wall panels in shower areas (R702.4.2).

- Plumbing fixtures shall comply with the following conservation requirements:  Water closets-Tank type 1.6 gal. /flush. Shower heads- 2.5 gal. /minute. Faucets- 2.2 gal. /minute, provide aerator. (Table P2903.2.).

- Water treatment systems- shall be equipped with an automatic or readily accessible manual shutoff to prevent continuous flow when not in use. (N1103.4.1).

- Domestic dishwashing machines connected to a disposer shall have the discharge installed as high as possible. (P2717.3).

- Storage-tank type water heaters shall be installed with a drain pan and drain line. (P2801.5.1-.2).

- The hot water circulating system shall be equipped with an automatic or readily accessible manual on switch and a temperature sensor activated shut-off that can automatically turn off the hot-water circulating pump when the set temperature is reached. N1103.4.1 amended.

- Provide roof/attic ventilation unless insulation is applied directly to underside of roof sheathing or the dimension is 24 inches or less between the ceiling and bottom of roof sheathing. (R806.1 Amended).

- Energy compliance shall be demonstrated by a passing REScheck energy compliance score. (N1101.2).

- Provide Minimum R-3 insulation on hot water pipes. (N1103.4).

- Supply and return ducts shall be insulated to a minimum R-8.  Ducts in floor trusses, minimum R-6. (N1103.2.1).

- Registers, diffusers and grilles shall be mechanically fastened to rigid supports or structural members on at least two opposite sides in addition to being connected to the ductwork they serve.

- Dryer exhaust ducts shall conform to the requirements of Sections (M1502.4.5 amended), M1502.4.1 thru M1502.4.6.

- Exhaust air from kitchens, bathrooms and toilet rooms shall not be re-circulated within a residence or to another dwelling unit, shall not discharge into an attic and/or crawl space and shall be exhausted directly to the outdoors. (M1507.2).

- Electrical fixtures located in damp or wet locations shall be “listed” to be suitable for such location. (E4003.9).

- Provide a wall mounted GFCI protected receptacle outlet within 36” of a bathroom or powder room lavatory.  (E3901.6).

- 15- and 20-ampere receptacles installed in bathrooms, garages and grade-level portions of unfinished accessory buildings used for storage or work areas, and installed outdoors shall have GFCI protection for personnel. (E3902.1-.3).

- All branch circuits that supply 15- and 20-ampere outlets installed in family rooms, dining rooms, living rooms, parlors, libraries, dens, bedrooms, sunrooms, recreations rooms, closets, hallways and similar rooms or areas shall be protected by a combination type arc-fault circuit interrupter (AFCI) installed to provide protection of the branch circuit. (E3902.12).

- In areas specified in Section E3901.1, 15- and 20-ampere receptacles shall be listed tamper-resistant. (E4002.14).

- Provide Smoke Alarms in new and existing areas of home.  (R314).

- Approved carbon monoxide alarms shall be installed outside of each separate sleeping area in the immediate vicinity of the bedrooms in dwelling units within which fuel-fired appliances are installed and in dwelling units that have attached garages. (R315).

- Provide a switch for the stairway when there are 6 or more risers.  (R303.7.1).

- Receptacle outlets shall be installed so that no point along the floor line in any wall space is more than 6 feet, measured horizontally, from an outlet in that space, including any wall space 2 feet or more in width. (E3901).

- Provide a minimum of two 20-amp small appliance branch circuits for the kitchen/dining/breakfast. (E3703.2).

- Provide a concrete encased grounding electrode of not less than 20 feet of #4 bare copper. (E3608.1.2).

- Provide bonding to the water piping, gas and metal building systems. (E3606.9, E3609.7).

- All metal piping systems, metal parts of electrical equipment, and pump motors associated with the hydro massage tub shall be bonded together using a copper bonding jumper, insulated, covered, or bare, not smaller than No. 8 solid.  (E4209).

- A minimum of 75 percent of the lamps in permanently installed lighting fixtures shall be high-efficacy lamps or a minimum of 75 percent of the permanently installed lighting fixtures shall contain only high-efficacy lamps. (N1104.1).

- Recessed luminaires installed in the building thermal envelope shall be IC-rated, labeled with air leakage rate not more than 2.0 cfm... sealed with a gasket or caulk between the housing and the interior wall or ceiling covering.  (N1102.4.4).

- Provide outside combustion air to all indoor fireplaces, with air intake located not higher than the firebox. (R1006.2).

- Where a listed decorative appliance is installed, the fireplace damper shall be afixed open and shall comply with the listed decorative appliance manufacture’s installation instructions. (G2434, G2435, G2453.1).

- At least one thermostat shall be provided for each separate heating and cooling system.  (N1103.1).

- The building shall be provided with ventilation that meets the requirements of Section M1507 or with other approved means of ventilation. Outdoor air intakes and exhausts shall have automatic or gravity dampers that close when the ventilation system is not operating. (N1103.5).

- The building or dwelling unit shall be tested and verified as having an air leakage rate of not exceeding 5 air changes per hour.  Testing shall be conducted with a blower door at a pressure of 0.2 inches w.g. (50 Pascals).  Testing shall be conducted by an approved third party. A written report of the results of the test shall be signed by the party conducting the test and provided to the building official. Testing shall be performed at any time after creation of all penetrations of the building thermal envelope. (N1102.4.1.2).

- Ducts, air handlers, and filter boxes shall be sealed. Joints and seams shall comply with Section M1601.4.1, (N1103.2.2). Duct tightness shall be verified by either of the following:

        - Post-construction test: Total leakage shall be less than or equal to 4 cfm per 100 square feet of conditioned floor area when tested at a pressure differential of 0.1 inches w.g. (25 Pa) across the entire system, including the manufacturer’s air handler enclosure. All register boots shall be taped or otherwise sealed during the test.

        - Rough-in test: Total leakage shall be less than or equal to 4 cfm per 100 ft2 of conditioned floor area when tested at a pressure differential of 0.1 inches w.g. (25 Pa) across the system, including the manufacturer’s air handler enclosure. All registers shall be taped or otherwise sealed during the test. If the air handler is not installed at the time of the test, total leakage shall be less than or equal to 3 cfm per 100 square feet of conditioned floor area.